## Electrification Work
CIPET: SCHOOL FOR ADVANCED RESEARCH IN PETROCHEMICALS (SARP) - ARSTPS
GOVERNMENT OF INDIA
SECTION - I
SUPPLY, INSTALLATION, ERECTION & TESTING OF ELECTRIFICATION WORK AT CIPET:SARP ARSTPS
TECHNICAL BID
Tender No. | e-TENDER No. CIPET:SARP-ARSTPS/Elect.Work/2021-22/e-Ten-02
Items of Description | Supply, Installation, Erection & Testing of Electrification Work at CIPET:SARP ARSTPS
Sl.No | DESCRIPTION | Particulars |  | Remarks
I | Name of the Supplier
II | Postal address
III | Telephone No. with STD code
IV | Fax with STD code
V | Name of Contact person
VI | Mobile No.
VII | e-mail ID
VIII | BELOW GIVEN DOCUMENTS TO BE SCANNED AND UPLOADED IN THE WEBSITE www.tenderwizard.com/CIPET WITHIN THE PERIOD OF SUBMISSION.
1 | Certificates:
(i) | i) Registration Certificate if Any, with DPS/DGS&D/NSIC/MSME (Attach Proof)
(ii) | ii) PAN (Permanent Account Number) Registration (Attach Proof)
(iii) | iii) Certificate of Registration for GST (Attach Proof)
(iv) | iv) Authorization Certificate from Principal (if not manufacturer) (Attach Proof)
IX | Commericial Terms for Quoted items (Please Provide Commercial terms and conditions in the below form)
1 | Validity of Offer
2 | The Commerical quote should be INR only
3 | Terms of Payments :- 100% payment for actual Supply, Installation, Erection & Testing of Electrification Work / Material and other incidental services at site and submission of acknowledgement and report issued by the Purchaser’s representative.
4 | Delivery period (in days)
5 | Guaranty / Warranty(Please Indicate the Period)
6 | Whether All Documents Relating to tender Viewed | Yes / No
7 | Similar works carried-out by the Bidder in Government / Semi-Governments / Undertakings / Autonomous / Statutory Bodies / Local Bodies / Labs / R & D units / Institutions / Universities & Industries etc. (Attach proof) | Attached / Not Attached
8 | Furnish the information of last three years of similar work and satisfactory performance report in the proforma given under Section IX-A. | Attached / Not Attached
9 | Documentary evidence (Client’s Certificates) in support of the satisfactory work done as specified above. (Attach Proof) | Attached / Not Attached
10 | Technical Catalogue / leaflet clearly mentioning the Make / Model number, name of material and technical details. | Attached / Not Attached
11 | Auditor Certificate confirming the Turnover for the past three years / IT Returns for last three years ending March 31, 2020 | Attached / Not Attached
TECHNICAL SPECIFICATIONS
Sl.No | DESCRIPTION | UNIT | QTY. | Bidders Specifications | Remarks
ABBRIVATION : S E T C : Supply, erection, testing & Commissioning.
I.T.C : Installation, Testing & Commissioning.
E.T.C : Erection, Testing & Commissioning
I | PART-A
LT PANELS (COMMON SPECIFICATION)
Enclosure
The panel shall be front operated floor mounted , totally enclosed, compartmentalized,
vermin proof, indoor, cubicle type power panel.
For load bearing members- 16 SWG CRCA sheet.
Internal partition & doors - 16 SWG CRCA sheet .
The panel shall be fully powder coated after seven tank treatment. Color of the panel
shall be as per approval.Each door shall be casketed using nitrile rubber and hinged
on. each cubicle with insulated door knob. Danger sign board, earthing bus and lugs,
cable chamber, bus bar chamber with air vent with insect proof, aluminum anodized
name platesGland plate of all panels shall made out of 2mm thick aluminum Panel
shall have one empty chambers and bus bar expanding provision for future.
Cable chamber entry shall be provided at the top and bottom.Bus bar
Bus bar
Horizontal & vertical bus bars shall be aluminium sleeved as mentioned in line item.
Aluminium bus size shall be rated based on 0.8A/sq.mm.
Control and metering
LED indication lamps with necessary control MCBs for R,Y,B indication shall be
LED illuminated push buttons with necessary control FUSETBs for ON, OFF
All incomers shall have MFM capable to measure v,a,f
Measuring CT shall be of TAP type class 1.
1 | SUB PANEL
Incomer: 400A TPN MCCB 1NOS
RYB INDICATION WITH MFM METER V,A,F
Outgoings: -
160A ,TPN MCCB , -6NOS
100A ,TPN MCCB , -2 NOS
PANEL SIZE - 1750L X 1750H X 350D
SHEET THICKNESS - 1.6 MM
FLOOR OR WALL MOUNTED
ALUMINUM BUSBAR
| SIEMENS GREY POWDER COATING | Set | 1
PART-B DISTRIBUTION BOARDS
NOTE :
a | THE MCB' S IN THE MCB DB SHALL BE OF APPROPRIATE DUTY
(CURVE) DEPENDING ON THE CONNECTED LOAD.THE MCB SHALL
BE OF 10KA RUPTURING CAPACITY.
b | THE MCB DB SHALL BE PROVIDED WITH SUITABLE BUS BARS,
INTERLINKS, NEUTRAL LINK, EARTH LINKS, EARTH LABELS,
DESIGNATION LABELS, COMPART- MENT &
INTER-COMPARTMENT SHROUDS ETC. AS PER REGULATORY
MEASURES AND THE SIZE OF THE DB's SHALL BE AS PER THE SITE
REQUIREMENT / CONDITION. THE DB's SHOULD BE INSTALLED
EITHER CONCEALED / SURFACE MOUNTED WITH REQUIRED
ACCESSORIES AS PER SITE CONDITION.
c | THE DB'S SPECIFIED HEREIN UNDER SHALL BE PROVIDED WITH
SUITABLE SIZE ADOPTER BOX WITH SHROUDED CONNECTOR SAND
WITH INTERCONNECT- ING SUITABLE SIZE SOLID LINKS / COPPER
WIRES TO TAKE THE AL. AR. CABLE AS SPECIFIED ELSE WHERE IN THE
TENDER.
1 | S E T C of 4 way Vertical DB
MCCB DB for Common Main DB for MJF Machine comprising of :-
1 - 100 A 4 Pole MCCB as incomer.
1 - 63 A TP MCB
1 - 32 A TP MCB
| 6 - 6A- 32 A SP MCB as outgoing to loads . | Set. | 1
2 | S E T C of 6/8 way Vertical DB
MCCB DB for Common Main DB for Injection Moulding M/c. comprising of :-
1 - 100 A 4 Pole MCCB as incomer.
3 - 32 A TP MCB
1 - 16 A TP MCB
| 6 - 10A- 32 A SP MCB as outgoing to loads . | Set. | 1
3 | S E T C of 4 way Vertical DB
MCB DB for Common Main DB for SLA Machine comprising of :-
1 - 63 A 4 Pole MCB as incomer.
1 - 25 A FP MCB as phase isolation .
| 9 - 6A- 10A SP MCB as outgoing to loads . | Set. | 1
4 | S E T C of compartmental type MCCB Enclosure industrial pattern MCB
DB for Emergency.. (with C curve MCB's) comprising of :-
| 1 - 100 A FP MCCB as incomer for the UPS | Sets | 1
PART-C CABLES / TERMINATIONS / WIRES /CABLE
TRAY/ MARKERS / PUSH BUTTON STATION
LT CABLES
1 | Supply and laying of following sizes of 1.1KV grade XLPE insulated armoured
FRLS grade cable with aluminium/ copper conductor multistrand cable with ISI
markings of approved make and quality from Main MV to various switch
boards / Distribution boards / Power loads. The cable shall be laid in the
earthern trenches / already built masonry trench / cable trays, racks
(excluding supply & erection of cable trays / racks) Wherever the cables
arelaid in earthern trenches the cable shall laid in the ground at a depth of
not less than 1.0 Mt. from the vergin/road level as per site condition. The
scope includes excavation/refilling the trench after due laying of cable above
the sand cushoning supply & providing protective brick cover etc. in all
types of soil and strictly in conforminity regulatory norms. The rate quoted
also shall exclude escavation, supply providing brick covering, refilling the
trench after laying of cable providing necessary Road cross/ protection
stoneware / hume pipes. Wherever cable are required to be laid on wall, base
bracket fitted onto wall / ceiling and necessary clamps/ harwares etc. all
complete and the rate for such clamps, hardwares shall be included in the
scope. Before laying the cable approval for the routing and the manner of
laying shall be obtained from the Architect / Owner.
a) | 3 1/2 C 240 Sqmm. AL. AR . UG Cable | Mtrs. | 1
b) | 3 1/2 C 70 Sqmm . AL. AR . UG Cable. | Mtrs. | 1
c) | 3 1/2 C 50 Sqmm. AL. AR . UG Cable. | Mtrs | 1
d) | 5C 1.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
e) | 1C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
f) | 3C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
g) | 4C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
h) | 1C 4.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
i) | 4C 4.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
2 | LT CABLE TERMINATION
Supply and providing cable end termination for following sizes of 1100V
grade XLPE insulated armoured FRLS grade aluminium conductor
multi-strand cable with necessary gland sand jointing materials etc. all as per
requirement.
a) | 3 1/2 C 240 Sqmm. | Mtrs. | 1
b) | 3 1/2 C 70 Sqmm. | Mtrs. | 1
c) | 3 1/2 C 50 Sqmm. | Mtrs. | 1
d) | 5C 1.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
e) | 1C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
f) | 3C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
g) | 4C 2.5 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
h) | 1C 4.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
i) | 4C 4.0 Sqmm multi-strand FRLS copper conductor flexible Cable | Mtrs. | 1
PART-D LIGHTING POINTS
1 | POWER RECEPTCLES
a) | Supply & fixing 6A 5 pin shuttered socket outlet with a controlling 6A
single way control switch in its having earth stud at locations required. As per site conditions.
| conditions. | Nos | 1
b) | Supply & fixing 6/16A 5 pin shuttered socket outlet with a controlling 16A
single way control switch in its having earth stud at locations required. As per site conditions.
| conditions. | Nos | 1
c) | Supply & fixing 1 nos of 32 A Industrial socket outlet with a controlling 32A DP
MCB single way control switch in its having earth stud at locations required. As per
| site conditions. | Nos | 1
d) | Supply & fixing 1 nos of 63 A Industrial socket outlet with a controlling 63A FP
MCB single way control switch in its having earth stud at locations required. As per
| site conditions. | Nos | 1
2 | POWER WIRING
a) | Supply and wiring for 2R of 2.5 +1R of 1.5 Sqmm multi-strand FRLS copper
conductor 660V grade wire in concealed ISI marked suitable size PVC conduit
with all standard accessories all complete as required for 6 / 16A Power
| sockets of primary points,etc.. | Mtrs. | 1
b) | Supply and wiring for 2R of 4.0 +1R of 2.5 Sqmm multi-strand FRLS copper
conductor 660V grade wire in concealed ISI marked suitable size PVC conduit
with all standard accessories all complete as required for 6 / 16A power
| sockets of primary points,etc.. | Mtrs. | 1
c) | Supply and wiring for 2R of 6.0 +1R of 4.0 Sqmm multi-strand FRLS copper
conductor 660V grade wire in concealed ISI marked suitable size PVC conduit
with all standard accessories all complete as required for 6 / 16A power
| sockets of primary points,etc.. | Mtrs. | 1
d) | Supply and wiring for 4R of 16.0 +1R of 10.0 Sqmm multi-strand FRLS copper
conductor 660V grade wire in concealed ISI marked suitable size PVC conduit
with all standard accessories all complete as required for 6 / 16A power
| sockets of primary points,etc.. | Mtrs. | 1
PART-E EARTH & EARTH CONNECTION
1 | Supply and providing "ASHLOK"/EQUIVALENT OF 80mm dia and 3mtrs
lenth earth electrode arranged as per IS 3043-1987 including providing
necessary charcoal clay, salt etc. including all civil works like escavation
| masonary providing cast iron cover / slab etc. all complete. | Nos | 1
2 | Supply and run of following sizes of copper flat from earth electrode to
neutral terminals of transformer and other requried locations as per statutory
requirements and neatly clamped to wall, cable tray with necessary hardwares,
PVC Conduits at places required as directed by Architects / Consultants.
a) | 25 x 3 mm GI. flat. | Mtrs. | 1
b) | 1 RUN of 10 Sq.mm CU Wire | Mtrs. | 1
c) | Supply and laying of 25 x 3 mm Cu flat | Mtrs. | 1